## Lighting certification
GP1-MUR lighting - CE and UL/NRTL review, read off the submitted datasheets
A standard quoted in a spec is not a listing. Where a sheet only says "designed to UL8750" or "CSA C22.2", this reads Not stated. Most marks are logos, not words, so every row marked "Read by eye" was checked on the rendered page. Checked 30 Sep 2026.
Item | Group | Type | Description | Manufacturer | CE | UL / NRTL listing | Marks on the sheet | Where the evidence is | How established | What to do / watch | Datasheet
LUM3 | LUM | Luminaire | Indirect LED Strip - Eco Flex 240, 2700 K | LedFlex Group | Yes | UL badge shown, no file number | CE, UL, RoHS, LM79/80, TM66, CRI90+, IP20 | Badge strip, page 2 (logos) | Read by eye | The UL badge is a bare logo with no listing wording or file number. Ask LedFlex for the UL file/report before relying on it. | Open
LUM3.1 | LUM | Driver / power supply | Indirect LED Strip Driver, 30 W - EcoPac ELED-30-24DP2 | EcoPac Power | Yes | Not stated | CE, SELV, IP20, NFC, DALI-2 | Badge row under the product photo, page 2 (logos) | Read by eye | UK driver. CE only - which is EcoPac's own declaration, not a third-party listing. No NRTL mark, though the input is 100-277 VAC and so covers US voltages. | Open
LUM3.2 | LUM | Driver / power supply | Indirect LED Strip Driver, 100 W - EcoPac ELED-100-24DP2 | EcoPac Power | Yes | Not stated | CE, SELV, IP20, NFC, DALI-2 | Badge row under the product photo, page 2 (logos) | Read by eye | CE is EcoPac's own declaration, not a third-party listing. | Open
LUM3.3 | LUM | Profile (extrusion) | Indirect LED Strip Profile - Pro 0209 | LedFlex Group | n/a | n/a | None | Whole sheet | Curated from the text | A bare aluminium extrusion. It carries no electrical listing because it is not an electrical product. Also flagged discontinued. | Open
LUM4 | LUM | Luminaire | LED Strip in Furniture, 2.93 W/ft - Eco Flex 240, 2700 K | LedFlex Group | Yes | UL badge shown, no file number | CE, UL, RoHS, LM79/80, TM66, CRI90+, IP20 | Badge strip, page 2 (logos) | Read by eye | As LUM3. | Open
LUM4.1 | LUM | Driver / power supply | Furniture Strip Driver, 30 W - EcoPac ELED-30-24DP2 | EcoPac Power | Yes | Not stated | CE, SELV, IP20, NFC, DALI-2 | Badge row under the product photo, page 2 (logos) | Read by eye | CE is EcoPac's own declaration, not a third-party listing. | Open
LUM4.2 | LUM | Driver / power supply | Furniture Strip Driver, 60 W - EcoPac ELED-60-24DP2 | EcoPac Power | Yes | Not stated | CE, SELV, IP20, NFC, DALI-2 | Badge row under the product photo, page 2 (logos) | Read by eye | CE is EcoPac's own declaration, not a third-party listing. | Open
LUM4.3 | LUM | Profile (extrusion) | Furniture Strip Profile - Pro 0209 | LedFlex Group | n/a | n/a | None | Whole sheet | Curated from the text | As LUM3.3. | Open
LUM5 | LUM | Luminaire | LED Strip in Furniture, 0.73 W/ft - Eco Flex 240, 2700 K | LedFlex Group | Yes | UL badge shown, no file number | CE, UL, RoHS, LM79/80, TM66, CRI90+, IP20 | Badge strip, page 2 (logos) | Read by eye | As LUM3. | Open
LUM5.1 | LUM | Driver / power supply | Furniture Strip Driver, 30 W - EcoPac ELED-30-24DP2 | EcoPac Power | Yes | Not stated | CE, SELV, IP20, NFC, DALI-2 | Badge row under the product photo, page 2 (logos) | Read by eye | CE is EcoPac's own declaration, not a third-party listing. | Open
LUM5.2 | LUM | Profile (extrusion) | Furniture Strip Profile - Pro 0209 | LedFlex Group | n/a | n/a | None | Whole sheet | Curated from the text | As LUM3.3. | Open
LUM6 | LUM | Luminaire | LED Strip in Furniture, IP65 - Eco Flex 240, 2700 K | LedFlex Group | Yes | UL badge shown, no file number | CE, UL, RoHS, LM79/80, TM66, CRI90+, IP20 | Badge strip, page 2 (logos) | Read by eye | As LUM3. | Open
LUM6.1 | LUM | Driver / power supply | Furniture Strip Driver, 30 W - EcoPac ELED-30-24DP2 | EcoPac Power | Yes | Not stated | CE, SELV, IP20, NFC, DALI-2 | Badge row under the product photo, page 2 (logos) | Read by eye | CE is EcoPac's own declaration, not a third-party listing. SEPARATELY: this driver is IP20 and its own sheet says "IP20 design for indoor installation", while it serves LUM6 at IP65 outdoors. Remote-mounting a driver indoors is normal, but confirm where this one actually sits. | Open
LUM6.2 | LUM | Profile (extrusion) | Furniture Strip Profile - Pro 0409 | LedFlex Group | n/a | n/a | None | Whole sheet | Curated from the text | As LUM3.3. | Open
LUM7 | LUM | Driver / power supply | Integrated Mini Downlight Driver, 350 mA - CC20-D-350-N | TCI | Not stated | UL Recognized Component (cURus) | cURus, RCM (AU), PSE (JP) | CERTIFICATIONS column, page 2, row CC30-D-350-NL | Curated from the text | RECOGNIZED COMPONENT, not Listed: valid only inside other listed equipment, not as a standalone device. The CERTIFICATIONS column shows no CE, though TCI is an EU maker and CE is compulsory for EU sale. | Open
LUM8 | LUM | Luminaire | Courtesy Wall Light - Profilo 1.0 BORTOP02-2K7 | Simes | Yes | Not stated | CE, RoHS, IP65 | Mark strip, page 2 (logos) | Read by eye |  | Open
LUM8.1 | LUM | Driver / power supply | Courtesy Wall Light Driver - Mini Jolly DALI 20 | TCI | Not stated | Not stated - CSA quoted as a STANDARD only | Declared to CSA C22.2 no. 223, EN 55015, EN 61000-3-2/3-3, EN 61347 | "Standards compliance" block, page 2 (text) | Curated from the text | Designed-to, not listed-by. No mark or file number on the sheet. | Open
LUM9 | LUM | Luminaire | Exterior Step LED Strip, IP67 - Eco Flex 240, 2700 K | LedFlex Group | Yes | UL badge shown, no file number | CE, UL, RoHS, LM79/80, IP67, CRI90+, TM66 | Badge strip, page 2 (logos) | Read by eye | As LUM3. | Open
LUM9.1 | LUM | Driver / power supply | Exterior Step Strip Driver, 30 W - EcoPac ELED-30-24DP2 | EcoPac Power | Yes | Not stated | CE, SELV, IP20, NFC, DALI-2 | Badge row under the product photo, page 2 (logos) | Read by eye | CE is EcoPac's own declaration, not a third-party listing. SEPARATELY: this driver is IP20 and its own sheet says "IP20 design for indoor installation", while it serves LUM9 at IP67 outdoors. Remote-mounting a driver indoors is normal, but confirm where this one actually sits. | Open
LUM9.2 | LUM | Profile (extrusion) | Exterior Step Strip Profile - Pro 0409 | LedFlex Group | n/a | n/a | None | Whole sheet | Curated from the text | As LUM3.3. | Open
LUM10 | LUM | Luminaire | Exterior Courtesy Wall Light - Tiny Short 05-E146-Z5-CL | LEDS C4 | Not stated | Not stated | IP66 IK10, Class I, RF 850C glow wire, EU energy label D | Technical features, page 2 (read by eye) | Read by eye | The sheet prints performance pictograms but NO certification mark at all. LedsC4 is a Spanish maker, so CE is compulsory for EU sale - but this datasheet does not state it. Ask for the Declaration of Conformity. | Open
LUM11 | LUM | Luminaire | Path Light - Sinia 600 mm Bollard 10-E033-60-CK | LEDS C4 | Not stated | Not stated | BREEAM, Class II, LED replaceable | Technical features, page 2 (read by eye) | Read by eye | As LUM10. | Open
LUM11.1 | LUM | Luminaire | Path Light, Alternate - 71-E649-60-OU | LEDS C4 | Not stated | Not stated | IP67, Class II, driver replaceable | Technical features, page 2 (read by eye) | Read by eye | As LUM10. | Open
LUM11.2 | LUM | Driver / power supply | Path Light Driver - Maxi Jolly SV DALI IPR1-70 | TCI | Yes | Not stated | ENEC 05, KEMA KEUR, RCM, EAC, EL, SELV 60V | Mark strip, page 2 (logos) | Read by eye | ENEC is the European third-party certification for control gear - stronger than a self-declared CE. No NRTL mark. | Open
LUM12 | LUM | Luminaire | Surface-Mounted Service Downlight - WAC FM-05RN | WAC Lighting | Not stated | ETL / cETL Listed | ETL, cETL, Wet Location Listed, ADA, Title 24 JA8 | "Standards" line, page 2 (text) | Curated from the text | ETL (Intertek) is an NRTL - equivalent standing to UL for code purposes. | Open
LUM13 | LUM | Luminaire | Indirect Wall Lamp - Foil 1A334-FOIL-US02 | Vibia | Not stated | Not stated | None printed | Pages 2-3 (read by eye) | Read by eye | The specified reference is the 120 V / 60 Hz US variant (1A334-FOIL-US02), so an NRTL listing would be expected - the sheet does not show one. Ask Vibia. | Open
LUM14 | LUM | Luminaire | Table Lamp for Minibar - Kelly Wearstler Una Small KW 3901ALB | Visual Comfort | Not stated | cETLus Listed | cETLus, DRY location | Mark strip, page 2 (logo) | Read by eye | Dry location only. | Open
LUM15 | LUM | Luminaire | Floor Lamp, Pool Terrace - Kando P111 | Bover | Yes | cETLus Listed | cETLus, CE, EAC | "Certifications" block, page 2 (logos) | Read by eye | 120 V 60 Hz, WET, IP-44. Supplied through Bover USA. | Open
LUM16 | LUM | Luminaire | Portable Lamp - Kando M40R | Bover | Yes | cETLus Listed | cETLus, CE, EAC | "Certifications" block, page 2 (logos) | Read by eye | Battery/USB-C portable lamp. | Open
L&L12 | L&L | Luminaire | Submersible Pool Fixture, Steps - L&L Bright 1.6 316L | L&L Luce&Light | Yes | cULus Listed, file E495946 | cULus Listed E495946, CE, ENEC, FCC, SAA, CB, RoHS, DALI-2 | Mark strip, page 6 (logos) | Read by eye | The strongest evidence in the set: a listing mark WITH a file number. | Open
L&L12.1 | L&L | Driver / power supply | Pool Fixture Driver, 30 W - AV0D024V03066 | L&L Luce&Light | Yes | PENDING - not yet granted | SAA, CE, CB, RoHS granted; UL, cUL, FCC and ENEC all marked "pending" | "Certificate" row, page 3 (text) | Curated from the text | READ THIS ONE. The sheet itself says UL and cUL are PENDING, so this driver is NOT UL listed today. It feeds L&L12, which is. | Open
L&L12.2 | L&L | Driver / power supply | Pool Fixture Driver, 60 W - AV0D024V06066 | L&L Luce&Light | Yes | cUL / UL listed per the certificate row | CE, ENEC, UL, cUL, FCC, SELV, DALI-2 | "Certificate" row, page 3 (text) | Curated from the text | Model AV0D024V06066. Its safety-standards line also cites UL8750 and CAN/CSA-C22.2 No. 250.13. | Open
L&L13 | L&L | Luminaire | Submersible Pool Fixture - L&L Bright 3.0 316L | L&L Luce&Light | Yes | cULus Listed, file E495946 | cULus Listed E495946, CE, ENEC, FCC, RoHS, DALI-2 | Mark strip, page 7 (logos) | Read by eye |  | Open
L&L13.1 | L&L | Driver / power supply | Pool Fixture Driver, 60 W - AV0D024V06066 | L&L Luce&Light | Yes | cUL / UL listed per the certificate row | CE, ENEC, UL, cUL, FCC, SELV, DALI-2 | "Certificate" row, page 3 (text) | Curated from the text | Same driver as L&L12.2. | Open
L&L14 | L&L | Luminaire | Vegetation Projector - L&L Pivot Mini | L&L Luce&Light | Yes | Not stated | CE, UKCA, CB, EAC, IP66, IK06, Class III | Mark strip, page 2 (logos) | Read by eye | EU/UK marks only. No NRTL mark. | Open
L&L17 | L&L | Luminaire | Sconce - L&L Ella OUT 1.0 | L&L Luce&Light | Yes | Not stated | CE, UKCA, EAC, IP65, IK08, Class I | Mark strip, page 2 (logos) | Read by eye | EU/UK marks only. The sheet is also annotated "DALI driver under review". | Open
L&L17.1 | L&L | Driver / power supply | Sconce Driver, 5-Protocol - WSDDV225PA | Wago | Not stated | Not stated - UL/CSA quoted as STANDARDS only | Declared to UL8750 + UL1310, CAN/CSA-C22.2 No.250.13 | Safety standards line, page 3 (text) | Curated from the text | Designed-to, not listed-by. No mark or file number. | Open
iGL1 | iGL | Luminaire | Recessed Ceiling Downlight 14° - iGuzzini Laser 25 Fixed Round | iGuzzini | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p1,2 (text) | Automatic text scan |  | Open
iGL2 | iGL | Luminaire | Laser 25 Plaster Frame, New Construction - iGuzzini BN-LAS25RT-NC | iGuzzini | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p2 (text) | Automatic text scan |  | Open
iGL3 | iGL | Luminaire | Recessed Ceiling Downlight 26° - iGuzzini Laser 38 Fixed Round, Base Output | iGuzzini | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p1,2 (text) | Automatic text scan |  | Open
iGL4 | iGL | Luminaire | Laser 38 Plaster Frame, New Construction - iGuzzini BN-LAS38RT-NC | iGuzzini | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p2 (text) | Automatic text scan |  | Open
iGL5 | iGL | Luminaire | Laser 38 Chicago Plenum Housing - iGuzzini BN-LAS38RT-CP | iGuzzini | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p2 (text) | Automatic text scan |  | Open
iGL6 | iGL | Luminaire | Recessed Ceiling Projector 24° - iGuzzini Palco Ø 19 mm | iGuzzini | Not checked | Not checked | No manufacturer sheet attached | Source PDF is one page | Curated from the text | The datasheet behind this item is the curated summary page only - there is no iGuzzini page behind it to read. The other seven iGuzzini items are cULus listed. | Open
iGL7 | iGL | Driver / power supply | Remote DALI Driver, 30 W - eldoLED ECOdrive 4450-0700-030-UNV-EDA | iGuzzini | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p2 (text) | Automatic text scan |  | Open
iGL8 | iGL | Driver / power supply | Remote DALI Driver, 19 W - eldoLED ECOdrive 4450-0350-019-UNV-EDA | iGuzzini | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p2 (text) | Automatic text scan |  | Open
LTRN1 | LTRN | Control | LTRN1 - DS - Lutron myRoom XC Processor - MP-1L-GCU | Not stated | Yes | cULus mark | cULus mark, CE marking, UKCA | cULus mark p2; CE marking p2; UKCA p2 (text) | Automatic text scan |  | Open
LTRN2 | LTRN | Driver / power supply | LTRN2 - DS - Lutron QS Power Supply - MQSPS-DH-1-30 | Not stated | Yes | Not stated | CE marking | CE marking p1 (text) | Automatic text scan |  | Open
LTRN3 | LTRN | Control | LTRN3 - DS - Lutron Feed-Through DIN Panel - PD4-36F-120 | Not stated | Not stated | cULus mark | cULus mark | cULus mark p2 (text) | Automatic text scan |  | Open
LTRN4 | LTRN | Control | LTRN4 - DS - Lutron Phase-Adaptive Power Module - MQSE-4A1-D | Not stated | Not stated | UL listing | UL listing | UL listing p4 (text) | Automatic text scan |  | Open
LTRN5 | LTRN | Control | LTRN5 - DS - Lutron Switching Power Module - MQSE-2S1-D | Not stated | Not stated | UL listing | UL listing | UL listing p4 (text) | Automatic text scan |  | Open
LTRN6 | LTRN | Control | LTRN6 - DS - Lutron Energi Savr Node DALI - QSN-1DALUNV-D | Not stated | Not stated | UL file number, UL listing, cULus mark | UL file number, UL listing, cULus mark | UL listing p3; cULus mark p3; UL file number p3 (text) | Automatic text scan |  | Open
LTRN7 | LTRN | Control | LTRN7 - DS - Lutron Alisse 1-Column Keypad - FIX-18-27 - HW-NW-KP-S1-E | Not stated | Not stated | cULus mark | cULus mark | cULus mark p2 (text) | Automatic text scan |  | Open
LTRN8 | LTRN | Control | LTRN8 - DS - Lutron Alisse 2-Column Keypad - FIX-18-27 - HW-NW-KP-S2-E | Not stated | Not stated | cULus mark | cULus mark | cULus mark p2 (text) | Automatic text scan |  | Open
LTRN9 | LTRN | Keypad | LTRN9 - DS - Lutron Alisse Keypad Base - HW-QS-B-S1 | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN10 | LTRN | Wallbox | LTRN10 - DS - Lutron Wallbox - EBB-1-SQ | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN11 | LTRN | Control | LTRN11 - DS - Lutron Radio Powr Savr Occupancy Sensor - LRF2-OCR2B-P-WH | Not stated | Yes | UL listing, cULus mark | UL listing, cULus mark, CE marking, UKCA | UL listing p2; cULus mark p2; CE marking p2; UKCA p2 (text) | Automatic text scan |  | Open
LTRN12 | LTRN | Control | LTRN12 - DS - Lutron QS Sensor Module - QSM2-XW-C | Not stated | Yes | cULus mark | cULus mark, CE marking | cULus mark p3; CE marking p3 (text) | Automatic text scan |  | Open
LTRN13 | LTRN | Control | LTRN13 - DS - Lutron Maestro Occupancy Switch - MS-OPS2-WH | Not stated | Not stated | UL listing | UL listing | UL listing p3 (text) | Automatic text scan |  | Open
LTRN14 | LTRN | Control | LTRN14 - DS - Lutron Claro Wallplate - CW-1-WH | Not stated | Not stated | UL listing | UL listing | UL listing p3 (text) | Automatic text scan |  | Open
LTRN15 | LTRN | Control | LTRN15 - DS - Lutron Palladiom Thermostat - FIX-28 - MWP-T-OHW-WH-A | Not stated | Yes | UL listing, cULus mark | UL listing, cULus mark, CE marking, UKCA | UL listing p2; cULus mark p2; CE marking p2; UKCA p2 (text) | Automatic text scan |  | Open
LTRN16 | LTRN | Control | LTRN16 - DS - Lutron Fan-Coil Controller - SMC55-MYRM | Not stated | Yes | UL listing, cULus mark | UL listing, cULus mark, CE marking | UL listing p3; cULus mark p3; CE marking p3 (text) | Automatic text scan |  | Open
LTRN17 | LTRN | Control | LTRN17 - DS - Lutron Contact-Closure Interface - QSE-IO | Not stated | Yes | UL listing | UL listing, CE marking | UL listing p2; CE marking p2 (text) | Automatic text scan |  | Open
LTRN18 | LTRN | Warranty document | LTRN18 - DS - Lutron Comercial System Warranty - LSC-L2-P8LTD | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN19 | LTRN | Receptacle | LTRN19 - DS - Lutron Palladiom USB Receptacle - LTR-15-CCTR-BL | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN20 | LTRN | Receptacle | LTRN20 - DS - Lutron Architectural Receptacle - LTR-15-TR-BL | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN21 | LTRN | Faceplate | LTRN21 - DS - Lutron Palladiom Faceplate - LWT-U-P-SB | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN22 | LTRN | Control | LTRN22 - DS - Lutron Nova T GFCI Receptacle - NTR-15-GFST-BL | Not stated | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p2; cULus mark p2 (text) | Automatic text scan |  | Open
LTRN23 | LTRN | Control | LTRN23 - DS - Lutron Nova T Architectural Plate - NT-R3-NFB-SB | Not stated | Not stated | UL listing | UL listing | UL listing p16,22,23,24 (text) | Automatic text scan |  | Open
LTRN24 | LTRN | Control | LTRN24 - DS - Lutron Grafik Eye Control Cable - GRX-CBL-46L-500 | Not stated | Not stated | UL listing, cULus mark | UL listing, cULus mark | UL listing p1,2,3,4; cULus mark p1,2,4 (text) | Automatic text scan |  | Open
LTRN25 | LTRN | Roller shade | LTRN25 - DS - Lutron Sivoia QS Roller Shade - Roller 100 | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN25.1 | LTRN | Shade bracketry | LTRN25.1 - DS - Lutron Sivoia QS Dual Shade Bracketry Kits - WIN-BRK | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN25.2 | LTRN | Driver / power supply | LTRN25.2 - DS - Lutron QS Link Shading Power Supply - QSPS-P1-1-35V | Not stated | Yes | UL listing, cULus mark | UL listing, cULus mark, CE marking | UL listing p2; cULus mark p2; CE marking p2 (text) | Automatic text scan |  | Open
LTRN26 | LTRN | Drapery track | LTRN26 - DS - Lutron Drapery Track System - D145 | Not stated | Not stated | Not stated | None found in the text | Text search, whole sheet | Automatic text scan |  | Open
LTRN26.1 | LTRN | Driver / power supply | LTRN26.1 - DS - Lutron QS Link Shading Power Supply - QSPS-P1-1-35V | Not stated | Yes | UL listing, cULus mark | UL listing, cULus mark, CE marking | UL listing p2; cULus mark p2; CE marking p2 (text) | Automatic text scan |  | Open
A | PL | Luminaire | Pool Light L09 - L&L Bright 1.6 316L | L&L Luce&Light | Yes | cULus Listed, file E495946 | cULus Listed E495946, CE, ENEC, FCC, SAA, CB, RoHS, DALI-2 | Mark strip, page 5 (logos) | Read by eye | Submersible pool fixture. Same listing as L&L12 - a listing mark WITH a file number. | Open
B | PL | Luminaire | Pool Light L09.1 - L&L Bright 3.0 316L | L&L Luce&Light | Yes | cULus Listed, file E495946 | cULus Listed E495946, CE, ENEC, FCC, RoHS, DALI-2 | Mark strip, page 6 (logos) | Read by eye | Submersible pool fixture. Same listing as L&L13. | Open

## How to read it
Column | What it means
CE | A SIGNATURE, NOT A TEST. The manufacturer declares the product meets the applicable EU directives and signs a Declaration of Conformity. No third party tests it, there is no file number and there is no register to look it up in. Yes = a CE or UKCA mark appears on the sheet. Not stated = it does not, which is not the same as 'not CE marked'. Nothing 'lists' a CE mark.
UL / NRTL listing | A TEST. A Nationally Recognized Testing Laboratory tested the product, keeps a file on it and audits the factory - UL, ETL (Intertek) or CSA - and it comes with a file number you can look up. Only a LISTING counts here. cURus = Recognized Component, valid only inside other listed equipment, not as a standalone device.
Why they are separate columns | Neither substitutes for the other, and a CE mark is not a weaker grade of a UL listing - it is a different kind of claim, made by a different party.
Green | Both a CE/EU mark and an NRTL listing are stated.
Amber | One of the two is stated.
Red | Neither is stated, or a listing is marked pending.
Grey | Not an electrical product - a bare extrusion carries no listing.
Two traps this review was built to avoid
A standard is not a listing | "Standards compliance: CSA C22.2 no. 223" and "Safety standards ... UL8750 UL1310" say what a product was designed to. Anyone may write that. A listing is a body saying it tested the thing, and it comes with a mark and usually a file number.
The marks are pictures | Most of these sheets carry their marks as logos, so searching the text finds nothing on a sheet that plainly shows CE and UL. Rows marked 'Read by eye' were checked on the rendered page.